## Summary
Project Known Issues — Eastsound WWTP Upgrade Phase I (five lanes combined)
Measure | Value (formula)
Method themes (combined) | 31
Lane method items | 61
Lane method items not mapped to a theme | 0
Themes with no Issues Log entry | 0
Open document decisions | 139
Decisions with no Issues Log entry | 0
Decisions that are also Exception Report rows | 46
Settled or record-only items | 17
Open decisions — Civil & Site | 23
Open decisions — Process & Mechanical | 40
Open decisions — Electrical & Controls | 22
Open decisions — Structural & Building | 23
Open decisions — Contract & General | 31

## Method Issues
Theme | Combined issue | Lane items | Fix (proposed) | Owner | Status | Issues Log #
T01 | Drawing images too coarse (about 80 dpi) for small text | Structural & Building:Known 1; Civil & Site:K-03 | Native PDFs via SharePoint; re-run the S/A visual pass and re-tag | SharePoint | Deferred | #10, #54
T02 | S-sheet pages have no text layer | Structural & Building:Known 2 | OCR native PDFs; stage text beside each page | SharePoint | Open | #60
T03 | Library files named .pdf are not PDFs | Structural & Building:Known 3; Contract & General:W10 | Open-as-bundle and split-by-header steps in the crawl prompt; detect format by content at ingest | Setup | Worked around | #61
T04 | Spec text from other projects; pointers to sections, sheets and attachments that do not exist | Structural & Building:Known 4; Contract & General:W5 | Check every named structure, sheet and section against 01/02; never create rows from misses | Composer | Open | #52, #62
T05 | Upstream index statement contradicted by the source (01 log #12) | Structural & Building:Known 5 | Setup amends 01; crawl rule to log index corrections | Setup | Open | #51
T06 | Addendum changed drawings but not the matching spec text | Structural & Building:Known 6 | Supersession search step for every attribute Add. 4 changes | Composer | Worked around | #63
T07 | Weakest-tag rule: the bid item basis pulls every row to Inferred | Structural & Building:Known 7; Contract & General:W3; Civil & Site:K-01; Process & Mechanical:Test-bed 1; Process & Mechanical:Test-bed 7 | Separate Bid Item basis / classification confidence column | Composer | Open | #12
T08 | Submittal and Testing Y/N: source rule, third value, drawing-note and cross-lane requirements | Structural & Building:Known 8; Contract & General:W8; Civil & Site:CS-37; Civil & Site:K-09; Process & Mechanical:Test-bed 6; Electrical & Controls:Method 6 | Y / N / Not stated with a basis qualifier; owning lane sets the flag | Composer | Open | #13
T09 | Testing/Startup column undefined | Structural & Building:Known 9 | Define the column or split it | Composer | Open | #64
T10 | No quantity or unit column | Structural & Building:Known 10 | Add Qty and Unit columns | Composer | Open | #65
T11 | Spec-only rows have no Drawing Sheets value | Structural & Building:Known 11 | Allow "(reference only)" sheets or a Referenced Sheets column | Composer | Open | #66
T12 | Tag naming: free-text PROPOSED tags, sheet-scoped and duplicate printed IDs | Structural & Building:Known 12; Electrical & Controls:Method 3; Civil & Site:K-06; Process & Mechanical:Test-bed 4 | Naming rule or shared tag registry; tag-harvest pass; crosswalk before combining | Composer / Setup | Open | #2, #5
T13 | Owning lane lives in Notes, not a column | Structural & Building:Known 13 | Add an Owning Lane column | Composer | Open | #67
T14 | Row granularity uneven (components vs package rows; roll-ups; category rows) | Structural & Building:Known 14; Contract & General:W9; Electrical & Controls:Method 5 | One split rule in the schema | Composer | Open | #68
T15 | Area names uncontrolled | Structural & Building:Known 15 | Controlled Area list from 01 | Setup | Open | #7
T16 | Issue references by position; lane issue numbers not stable | Structural & Building:Known 16; Electrical & Controls:Method 4 | Permanent issue IDs; cite by ID and title | Composer | Open | #6, #69
T17 | Wiki Tags mix printed references with by-subject links; appendices linked only by subject | Structural & Building:Known 17; Contract & General:W6 | Split Tags into Cited and Related by subject | Composer | Open | #70
T18 | Notation and encoding (UTF-8 without BOM; ft/in vs marks) | Structural & Building:Known 18; Process & Mechanical:Test-bed 8 | xlsx view for people, CSV for machines; one dimension notation | Composer | Worked around | #71
T19 | Per-turn tool budget ended turns before saves | Structural & Building:Known 19; Process & Mechanical:Test-bed 5 | Save first; batches of about 8 units; reserve the last calls | All threads | Worked around | #1, #72
T20 | Visual pass drives the cost | Structural & Building:Known 20 | Native text layers; pre-rendered standard crops | Setup / SharePoint | Open | #73
T21 | The crawl needs a code sandbox | Structural & Building:Known 21 | Setup stages splits and crops so crawl threads only read | Setup | Open | #74
T22 | Existence and absence checks need a full-text search | Structural & Building:Known 22; Contract & General:W7 | Cross-reference and absence index in 02 | Setup | Open | #75
T23 | Concurrent sessions wrote the same working folder | Contract & General:W1; Contract & General:W2 | One folder per session; lock with session ID, heartbeat and content hash | All threads | Worked around | #76
T24 | Duplicate spec text double-counts requirements | Contract & General:W4 | Duplicate-body check; key requirements to the primary copy | Composer | Open | #77
T25 | Lane-wide requirements sit as prose, not Requirements rows | Contract & General:W11 | Crawl writes Requirements rows | Composer | Open | #14
T26 | Read method misses image-only content; text layer pairs tags wrongly | Electrical & Controls:Method 1; Electrical & Controls:Method 2; Civil & Site:CS-05; Civil & Site:CS-11; Process & Mechanical:Test-bed 3 | "Text + Visual" read method; image governs pairings | Setup | Open | #11
T27 | Partial reads: long sections scanned by key terms; Appendix C read by section | Electrical & Controls:Method 7; Civil & Site:K-04 | Decide whether key-term scanning meets the standard | Owner (Carl) | Open — owner decision | #78
T28 | Tagging conventions to ratify (conflicted-attribute placement; WSDOT tag placement) | Electrical & Controls:Method 8; Civil & Site:K-02 | Composer ratifies one convention each | Composer | Open | #79
T29 | Inferred links and "New" status in the Civil & Site Ledger | Civil & Site:K-07; Civil & Site:K-08 | Confirm at Merge or by RFI where disputed | Merge | Logged | #80
T30 | Cross-lane items kept in Issues, not the Ledger | Civil & Site:K-05 | Merge pulls them from Issues | Merge | Done in Merge | #23
T31 | Schema column 14 name ("Tag level" in 03 vs the CSV header) | Process & Mechanical:Test-bed 2 | Align 03 with the schema file | Setup | Logged | #81

## Lane Method Items
Lane | Lane ID | Item | Severity | Theme | Issues Log #
Contract & General | W1 | Two sessions wrote the same working folder: duplicate ledger tags and diverging Issue numbers |  | T23 | #76
Contract & General | W2 | The lock's release rule (no file changed for 10+ minutes) relies on file timestamps, but notes 250 and 290 were rewritten by the other writer while still showing this session's original write time |  | T23 | #76
Contract & General | W3 | The weakest-tag rule leaves 0 of 49 rows Verified — bid item, area and discipline mappings are nearly always Inferred |  | T07 | #12
Contract & General | W4 | Duplicate text double-counts requirements (00 73 00 insert copy; 01 66 00 = 01 60 00; leakage test and barrier clauses twice) |  | T24 | #77
Contract & General | W5 | Checklist lines point to sections and attachments that don't exist |  | T04 | #52, #62
Contract & General | W6 | Appendices are never cited by name, so citation-following orphans them |  | T17 | #70
Contract & General | W7 | Proving absence ("the contract has no Ecology change-order step") needed a full-text search; the Wiki and Ledger can't answer it — a design gap under the retrieval rule |  | T22 | #75
Contract & General | W8 | Submittal and Testing Y come from category clauses ("all equipment") mapped to rows, not from items named in the text |  | T08 | #13
Contract & General | W9 | Component granularity is mixed: Train 3 basins, clarifier, 2W wet well and DO/pH sensors have their own rows; mixers, air lift pumps and valves stay in the package row |  | T14 | #68
Contract & General | W10 | File types don't match extensions: the main spec .pdf is plain text; Add. 4 and the QA plan .pdf are page bundles (text plus image per page) |  | T03 | #61
Contract & General | W11 | Lane-wide requirements (AIS, wages, O&M, record drawings, testing split, commissioning days) sit as prose in Issues §3, not as rows in `Requirements_Schema.csv` |  | T25 | #14
Electrical & Controls | Method 1 | Read method in 01 misses image-only content |  | T26 | #11
Electrical & Controls | Method 2 | Text-layer order pairs tags wrongly |  | T26 | #11
Electrical & Controls | Method 3 | PROPOSED tags assigned before the one-line was read |  | T12 | #2, #5
Electrical & Controls | Method 4 | Issue numbers are not stable |  | T16 | #6, #69
Electrical & Controls | Method 5 | Raceway runs are one roll-up row |  | T14 | #68
Electrical & Controls | Method 6 | Submittal and Testing columns are blank for other-lane equipment |  | T08 | #13
Electrical & Controls | Method 7 | Long spec sections were scanned, not read line by line |  | T27 | #78
Electrical & Controls | Method 8 | Where a conflicted attribute is tagged |  | T28 | #79
Civil & Site | CS-05 | G0.2 is flagged Text (832 body characters) but its legend descriptions and abbreviation list exist only in the page image (plans_1 p.2). |  | T26 | #11
Civil & Site | CS-11 | C1.3, C1.4, C1.5 and C2.4 pass the Text threshold on about 300 characters of UV equipment block labels; C1.5 elevations and C2.4 trench drains are graphics-only |  | T26 | #11
Civil & Site | CS-37 | Submittal and Testing/Startup columns follow spec sections only, so drawing-note and reference-document requirements show N: C0.5 demolition plan, G0.3 and Appe |  | T08 | #13
Civil & Site | K-01 | No Ledger row can reach Verified |  | T07 | #12
Civil & Site | K-02 | WSDOT tag placement |  | T28 | #79
Civil & Site | K-03 | Image legibility |  | T01 | #10, #54
Civil & Site | K-04 | Appendix C read by section |  | T27 | #78
Civil & Site | K-05 | Cross-lane items kept out of the Ledger |  | T30 | #23
Civil & Site | K-06 | Sheet-scoped tags |  | T12 | #2, #5
Civil & Site | K-07 | Inferred links in the Ledger |  | T29 | #80
Civil & Site | K-08 | 'New' status mostly Inferred |  | T29 | #80
Civil & Site | K-09 | Flags on cross-lane rows |  | T08 | #13
Process & Mechanical | Test-bed 1 | Weakest-tag rule vs 04 |  | T07 | #12
Process & Mechanical | Test-bed 2 | Schema column name |  | T31 | #81
Process & Mechanical | Test-bed 3 | Read Method gap |  | T26 | #11
Process & Mechanical | Test-bed 4 | Duplicate IDs |  | T12 | #2, #5
Process & Mechanical | Test-bed 5 | Tool budget |  | T19 | #1, #72
Process & Mechanical | Test-bed 6 | Y/N convention |  | T08 | #13
Process & Mechanical | Test-bed 7 | Instrument bid items |  | T07 | #12
Process & Mechanical | Test-bed 8 | CSV encoding |  | T18 | #71
Structural & Building | Known 1 | Drawing images too coarse for small text | High | T01 | #10, #54
Structural & Building | Known 2 | S sheets have no text layer | Medium | T02 | #60
Structural & Building | Known 3 | Library files named .pdf are not PDFs | Low | T03 | #61
Structural & Building | Known 4 | Spec text carried over from other projects | Medium | T04 | #52, #62
Structural & Building | Known 5 | Upstream index statement contradicted by the source | Low | T05 | #51
Structural & Building | Known 6 | Addendum changed the drawings but not the matching spec text | Low | T06 | #63
Structural & Building | Known 7 | The bid item drags every row down to Inferred | High | T07 | #12
Structural & Building | Known 8 | Y/N columns need a third value and a source rule | Medium | T08 | #13
Structural & Building | Known 9 | "Testing/Startup" is undefined | Medium | T09 | #64
Structural & Building | Known 10 | No quantity or unit column | Medium | T10 | #65
Structural & Building | Known 11 | Spec-only items have no Drawing Sheets value | Low | T11 | #66
Structural & Building | Known 12 | Free-text PROPOSED tags won't match across lanes | High | T12 | #2, #5
Structural & Building | Known 13 | Cross-lane owner lives in Notes | Low | T13 | #67
Structural & Building | Known 14 | Row granularity is uneven | Low | T14 | #68
Structural & Building | Known 15 | Area names go beyond sheet titles | Low | T15 | #7
Structural & Building | Known 16 | Issue references use list positions | Medium | T16 | #6, #69
Structural & Building | Known 17 | Wiki tags mix printed references with by-subject links | Low | T17 | #70
Structural & Building | Known 18 | Notation and encoding | Low | T18 | #71
Structural & Building | Known 19 | Per-turn tool budget | Medium | T19 | #1, #72
Structural & Building | Known 20 | The visual pass drives the cost | Medium | T20 | #73
Structural & Building | Known 21 | The process needs a code sandbox | Medium | T21 | #74
Structural & Building | Known 22 | Existence checks needed a whole-file search | Low | T22 | #75

## Decisions
# | Lane | Lane ID | Issue | Type | Priority | Impact | Resolver | Needed | Status | Exception Report # | Issues Log #
1 | Contract & General | 1.1 | Bid deadline: 10:00 AM vs 2:00 PM PST, Feb 8, 2023 | Conflict |  | Bid phase only | Owner | Addenda 1–3 or Owner confirmation | Open | — | #86
2 | Contract & General | 1.2 | Add. 4 is dated Feb 9, 2023, one day after the stated bid opening | Conflict |  | Bid phase; addenda completeness | Setup / Owner | Addenda 1–3 or the bid tabulation | Open | — | #86
3 | Contract & General | 1.3 | Contract signing window: 10 working days vs 10 calendar days | Conflict |  | Award | Owner/Engineer | Clarification | Open | — | #86
4 | Contract & General | 1.4 | Bid hold: award within 45 days vs acceptance within 60 days | Conflict |  | Bid phase only | Owner | Clarification (moot after award) | Open | — | #86
5 | Contract & General | 1.5 | Subcontractor list: all within 1 hour vs steel and rebar installers within 48 hours | Conflict |  | Bid phase only | Owner | Confirmation (low impact) | Open | — | #86
6 | Contract & General | 1.6 | DBE forms and Bidders List: with the bid vs within 1 hour after bid time | Conflict |  | Bid phase only | Owner | Clarification — 00 53 00 states both timings, so its precedence clause can't settle it | Open | — | #86
7 | Contract & General | 1.8 | Liquidated damages: General Conditions sum per calendar day vs LD = 0.15C/T per working day under WSDOT 1-08.9 | Conflict |  | Construction — cost exposure | Owner/Engineer | Ruling on day basis and amount; General Conditions and WSDOT 1-08.9 not staged | Open | — | #86
8 | Contract & General | 1.9 | County permit: approved June 2022 vs "currently processing" (Building Permit #21-0385) | Conflict |  | Before mobilization | Owner | Current permit status | Open | — | #86
9 | Contract & General | 1.11 | Guarantee: one year from Substantial Completion vs one year after District acceptance of all work | Conflict |  | Closeout — warranty and bond dates | Owner/Engineer | Ruling | Open | — | #86
10 | Contract & General | 1.14 | Contractor qualifications: with the bid vs within 24 hours of opening | Conflict |  | Bid phase only | Owner | Confirmation | Open | — | #86
11 | Contract & General | 1.16 | Field office is optional, but the schedule and records must be kept there | Conflict |  | Mobilization — general conditions cost | Owner | Whether a field office is required | Open | — | #86
12 | Contract & General | 1.17 | Substitution requests: 10 days after the Agreement vs 30 days after the Contract Date; PDF vs six copies | Conflict |  | Early procurement | Owner | Last day and format | Open | — | #86
13 | Contract & General | 1.19 | Temporary facilities out before the Substantial Completion request vs at completion or Final Completion | Conflict |  | Closeout — demob timing | Owner | SC 19 governs temporary pump and process equipment (Inferred); power, water and restrooms stay open | Open | #245 | #86
14 | Contract & General | 1.20 | Energy code: 2015 WSEC named vs the edition in effect on the bid date | Conflict |  | Closeout — Blower Building documents | Engineer | Edition used for design and permit #21-0385 (external, not staged) | Open | — | #86
15 | Contract & General | 1.21 | Dewatering start-up: "a minimum of one (2) days" per supplier | Conflict |  | Commissioning | Engineer | 1 or 2 days | Open | #190, #246 | #86
16 | Contract & General | 1.26 | QA plan requires Ecology review of significant change orders; the contract has no such step | Conflict |  | Change management | Owner | Funding-agreement requirement (not staged) | Open | — | #86
17 | Contract & General | 1.10 | Pre-construction meeting: within 2 weeks of award notice vs after NTP | Conflict |  |  | Owner/Engineer | SC 13 governs — SC 2 (p.88) ranks Supplemental Conditions above Technical Specifications, and Division 01 sits under the Part 3 Technical Specifications divider (p.122, per 02) | Working answer — confirm | — | #86
18 | Contract & General | 1.12 | Schedule and Schedule of Values due dates | Conflict |  |  | Owner/Engineer | SC 16 governs: CPM schedule at the pre-construction meeting; Schedule of Values within 10 working days of NTP | Working answer — confirm | — | #86
19 | Contract & General | 1.15 | WSDOT and APWA standard specifications: "latest edition" vs 2022 Edition | Conflict |  |  | Owner/Engineer | 2022 governs; whether 2022 was the edition in effect on the bid date is Unresolved (external, not staged) | Working answer — confirm | — | #86
20 | Contract & General | 1.23 | Progress meetings: weekly with the Owner presiding vs monthly with the Engineer conducting | Conflict |  |  | Owner/Engineer | 01 31 00 governs — the QA plan is not a Contract Document | Working answer — confirm | — | #86
21 | Contract & General | 1.24 | Earthwork sieve analyses: Owner's lab vs Contractor's QC lab | Conflict |  |  | Owner/Engineer | 01 45 00 governs; cost follows 01 45 00 | Working answer — confirm | — | #86
22 | Contract & General | 2.1 | Section 00 22 13 Supplemental Bidder Responsibility Criteria is cited but not in the manual | Missing information |  | Bid phase | Owner/Engineer |  | Open | — | #86
23 | Contract & General | 2.2 | DBE forms 6100-3 and 6100-4 are not bound; the pointers to Appendix G and to 00 73 00 Attachments 6–7 are wrong | Missing information |  | Bid phase | Owner / Setup |  | Open | — | #86
24 | Contract & General | 2.3 | EO 11246 "covered area" left as a placeholder | Missing information |  | Subcontract flow-down | Owner / Commerce |  | Open | — | #86
25 | Contract & General | 2.4 | Federal wage decision: Appendix E (WA20220057 Mod. 4, 12/23/2022, Heavy) is taken as the determination; whether it was current at bid opening, and whether a Building decision is also needed, are open | Missing information |  | Payroll compliance | Owner / Commerce |  | Open (partly closed) | — | #86
26 | Contract & General | 2.5 | Sections cited but not in the manual: 00 25 13, 00 43 36, 00 45 14, 01 30 00, 00 72 00, "00 73 00a" | Missing information |  | Bid phase and closeout | Engineer |  | Open | — | #86
27 | Contract & General | 2.6 | "General Conditions" are not in the library; the WSDOT Standard Specifications appear to serve (Inferred) | Missing information |  | Contract-wide | Setup / Owner |  | Open | #248 | #86
28 | Contract & General | 2.7 | The funding inserts (00 53 00, 00 54 00) are not ranked in the SC 2 order of precedence | Missing information |  | Contract-wide | Owner/Engineer |  | Open | — | #86
29 | Contract & General | 2.8 | Commissioning skips ¶1.08–1.09; no start-up paragraph for the generators, ATS, MCC, PLC panel, 480V service or influent sampler | Missing information |  | Commissioning | Engineer; Electrical & Controls |  | Open | #249 | #86
30 | Contract & General | 2.9 | Appendices D, E and I are never cited by name in Divisions 00–01; links run by subject | Missing information |  | Crawl design | Setup / Composer |  | Design note | — | #86
31 | Contract & General | 2.10 | QA plan cites WAC 173-351 for Contractor quality control, unlike its WAC 173-240 basis elsewhere | Missing information |  | Record / QA | Engineer |  | Open | — | #86
32 | Electrical & Controls | Issues #4 | Service load vs the 225 kVA utility transformer | Conflict (Engineer decision) |  | Utility coordination; service sizing | Engineer (RFI); OPALCO coordination per 26 05 00 ¶3.03 (main spec p.279) | Reconcile the MDP schedule with the load calculation and confirm the transformer size with OPALCO. | Unresolved | — | #84
33 | Electrical & Controls | Issues #2 | Influent pump starters: IPS panel or MCC | Conflict (Engineer decision) |  | Procurement — MCC units, IPS panel content, feeder routing; bears on the Add. 4 Clarification 4 MCC section count | Engineer (RFI) | Confirm where the influent pump starters sit. | Unresolved | — | #84
34 | Electrical & Controls | Issues #14 | Dewatering ventilation: continuous or only during dewatering, and how the fans are controlled | Conflict (Engineer decision) |  | Code and area classification; controls | Engineer (RFI) | Confirm continuous vs dewatering-only ventilation (it sets the E0.4 classification) and the fan control scheme. Related: airflow (item 20) and panel feed (item 8). | Unresolved | #26, #196, #248 | #84
35 | Electrical & Controls | Issues #7 | Level transducer ranges (0–15 psi vs 0–15 ft) and the digester intrinsic safety barrier | Conflict (Engineer decision) |  | Procurement (instrument range); controls | Engineer (RFI) | Confirm both ranges and whether the digester barrier is required. | Unresolved | #58 | #84
36 | Electrical & Controls | Issues #9 | Backup high-level floats start the wrong-size pumps | Conflict (Engineer decision) |  | Controls (hardwired backup sequence) | Engineer (RFI) | Confirm which pump each high-level float starts. | Unresolved | #40 | #84
37 | Electrical & Controls | Issues #12 | Low-level float on the E10.1 detail only | Conflict (Engineer decision) |  | Procurement (minor) | Engineer (RFI) | Confirm whether a low-level float is required (it would add a float, a PLC input and a barrier). | Unresolved | — | #84
38 | Electrical & Controls | Issues #13 | Effluent meter vault: Class I Div 2 or unclassified | Conflict (Engineer decision) |  | Installation and code (seal-offs, wiring method) | Engineer (RFI) | Confirm the wiring method at the effluent vault. | Unresolved | — | #84
39 | Electrical & Controls | Issues #11 | Ventilation control panel fed from LP1 or LP2 | Conflict (Engineer decision) |  | Installation (circuit source and run length) | Engineer (RFI) | Confirm the source panel and circuit. | Unresolved | — | #84
40 | Electrical & Controls | Issues #1 | Blower Building raceway concealment in a metal building | Conflict (Engineer decision) |  | Installation (raceway method in the Blower Building) | Engineer (RFI); cross-lane Structural & Building | Confirm how Blower Building raceway is concealed or run. | Unresolved | #192 | #84
41 | Electrical & Controls | Issues #3 | 2W pump tags and conduit count | Conflict (Engineer decision) |  | Documentation; installation (one or two conduits) | Engineer (RFI) | Confirm the tags and shared vs separate conduit. | Unresolved | #45, #193 | #84
42 | Electrical & Controls | Issues #10 | Influent pump 2 input list | Conflict (Engineer decision) |  | Controls; documentation | Engineer or system integrator | Corrected pump 2 input list. | Unresolved | — | #84
43 | Electrical & Controls | Issues #6 | Main PLC input numbering on E7.3 | Conflict (Engineer decision) |  | Controls; documentation | Engineer or system integrator | Corrected numbering and confirmed card count. | Unresolved | — | #84
44 | Electrical & Controls | Issues #19 | Temporary generator rating | Missing information |  | Bid and pricing | Engineer (bidder question) | Required rating at 480Y/277V, runtime or refuel expectation, and rental duration. | Unresolved | #14, #198 | #84
45 | Electrical & Controls | Issues #18 | Train 1 and 2 future provisions | Missing information |  | Bid and pricing; MCC section count | Engineer (bidder question) | State whether Phase I furnishes the MCC units, feeders and PLC inputs for Trains 1 and 2. | Unresolved | #197 | #39, #84
46 | Electrical & Controls | Issues #17 | UV-area pole light has no circuit | Missing information |  | Installation | Engineer (RFI) | Panel and circuit for the pole light and its receptacle. | Unresolved | — | #84
47 | Electrical & Controls | Issues #20 | Three items with no governing Division 26 section | Missing information |  | Procurement (who furnishes); Ledger Submittal/Testing columns | Engineer or Merge | Name the governing specification or furnisher for each. | Unresolved | #199 | #84
48 | Electrical & Controls | Known 17 | Temporary generator bid item | Bid item flag |  | Bid and pricing | Owner and Engineer (flag already in 02 Merge item 1, 03, 04 Bid Item #18) | Settle which bid item carries the temporary generator. | Unresolved | — | #84
49 | Electrical & Controls | Known 18 | Permanent generator bid item | Bid item flag |  | Bid and pricing | Owner and Engineer (flag already in 03 and 04 Other bid-item conflicts #1) | Settle the bid item. | Unresolved | — | #84
50 | Electrical & Controls | Issues #22 | Generator pad: civil or structural | Cross-lane conflict |  | Scope split | Merge — Civil & Site; Structural & Building | Confirm which sheet governs and carry the rebar bond. | Unresolved | #201 | #84
51 | Electrical & Controls | Issues #26 | Dewatering fan airflow for 6 air changes per hour | Cross-lane conflict |  | Code and area classification | Merge — Process & Mechanical (23 34 00) | Fan cfm and building volume from Process & Mechanical. | Unresolved | #205 | #84
52 | Electrical & Controls | Issues #27 | 2W hot box re-orientation | Cross-lane conflict |  | Installation (conduit, heat trace) | Merge — Civil & Site | Which hot box moves, and any conduit or heat-trace changes for this lane. | Unresolved | #206 | #84
53 | Electrical & Controls | Issues #32 | Who installs the Owner-furnished samplers | Cross-lane conflict |  | Scope split | Merge — Process & Mechanical | Assign the installation to a lane. | Unresolved | #13, #211 | #84
54 | Civil & Site | CS-13 | Buried valve list doesn't agree | Conflict | High | Valve and marker counts and valve types for procurement. | Engineer (RFI) | Governing valve list and marker count. | Unresolved | #177 | #82
55 | Civil & Site | CS-15 | Train 2 and Train 3 flow meter isolation valves: type and count | Conflict | High | 2 vs 4 valves; gate vs plug. | Engineer (RFI) | Valve type and count at each vault. | Unresolved | — | #82
56 | Civil & Site | CS-16 | Flow meter vault pipe labeled both force main and gravity | Conflict | High | Pipe class, fittings and test pressure through the vaults. | Engineer (RFI) | Service and pipe class. | Unresolved | #81 | #82
57 | Civil & Site | CS-29 | Buried pipe materials on C1.3 differ from Division 33 | Conflict | High | Pipe material procurement for five lines; Add. 4 changed only ID 10. | Engineer (RFI) | Material for IDs 12, 15, 19, 20, 21. | Unresolved | #85, #93, #94, #159 | #82
58 | Civil & Site | CS-35 | Storm drain SD-1 material not stated; cover looks shallow | Missing information | High | Possible DI pipe and CDF encasement not shown on the drawings (cover estimate Inferred; pipe OD not stated). | Engineer (RFI) | SD-1 material and any CDF. | Unresolved | — | #82
59 | Civil & Site | CS-31 | Footing drain pipe type | Conflict | High | Drain pipe and envelope material for the retaining wall and structures. | Engineer (RFI) | Pipe type and envelope. | Unresolved | — | #82
60 | Civil & Site | CS-33 | Groundwater elevation in NAVD88; drawings on NGVD 1929 | Conflict | High | Dewatering design: 31 23 19 requires dewatering 2 ft below structure bases, which can't be checked without a datum conversion. | Engineer or surveyor (RFI) | NAVD88–NGVD29 conversion for the site. | Unresolved | — | #82
61 | Civil & Site | CS-23 | Native material in trench backfill | Conflict | High | Import vs reuse of native soil; haul-off quantities. | Engineer (RFI); Contract & General for precedence (00 73 00) | Governing requirement, plus the order-of-precedence clause. | Unresolved | #138, #140, #152, #248 | #82
62 | Civil & Site | CS-24 | Trench compaction targets | Conflict | High | QA acceptance criteria for density testing (31 20 00). | Engineer (RFI) | Compaction targets by zone. | Unresolved | — | #82
63 | Civil & Site | CS-25 | Pay basis for dewatering and construction stormwater | Conflict | High | Which bid item carries dewatering and stormwater management. | Contract & General | Pay item. | Unresolved | #69, #153 | #82
64 | Civil & Site | CS-32 | Who provides construction staking | Conflict | High | Survey cost and responsibility. | Contract & General (00 73 00, Supplementary Conditions No. 7, cited by G0.3) | Responsible party. | Unresolved | #154 | #49, #82
65 | Civil & Site | CS-09 | Plant drain pump station isn't defined in this lane | Missing information | High | Possible scope gap; demolition of SSMH 1286 waits on it. | Engineer (RFI); Process & Mechanical via Merge | Sheet, tag and force main for the plant drain pump station. | Unresolved | #37, #151, #222 | #82
66 | Civil & Site | CS-27 | Stabilized construction entrance type | Conflict | Medium | Temporary works cost and submittal. | Engineer (RFI) | Whether plates replace or add to the spall entrance. | Unresolved | — | #82
67 | Civil & Site | CS-28 | Tracer wire spec, spacing and scope | Conflict | Medium | Wire procurement and which pipes get it. | Engineer (RFI) | Governing wire spec and scope. | Unresolved | — | #82
68 | Civil & Site | CS-19 | Yard hydrant detail and post hydrant size/location | Missing information | Medium | Hydrant type, accessories and hoses (33 31 00 ¶2.01 J–K). | Engineer (RFI); C1.1 (unavailable) may show it | Detail per location; post hydrant size and location. | Unresolved | — | #82
69 | Civil & Site | CS-34 | Groundwater log has no well ID or reference elevation | Missing information | Medium | Seasonal-high groundwater elevation for dewatering; pairs with CS-33. | Engineer (RFI) | Well ID and reference elevation. | Unresolved | — | #82
70 | Civil & Site | CS-01 | Catch basin removed under C0.5 Keyed Note 9 not identified | Missing information | Medium | Demolition scope and tie-ins. | Engineer (RFI); C2.1/C2.3 (unavailable) may show it | Structure ID. | Unresolved | — | #82
71 | Civil & Site | CS-14 | Valve schedule points to the wrong location sheets | Conflict | Low | Wrong reference only. | Engineer | Correct sheet reference. | Unresolved | — | #82
72 | Civil & Site | CS-17 | Yard hydrant detail points to the storm sheet | Conflict | Low | Wrong reference only. | Engineer | Correct sheet reference (C1.3 Inferred). | Unresolved | — | #82
73 | Civil & Site | CS-18 | 'Section 15051' cited but not in the manual | Missing information | Low | Pipe coding and identification requirement undefined. | Engineer | Governing section. | Unresolved | — | #82
74 | Civil & Site | CS-22 | Spec cross-references to sections that don't exist | Missing information | Low | Submittal and QC procedures point nowhere; intended sections look like 01 33 00, 01 45 00, 05 50 00, 03 30 00, 09 90 00 (Inferred); no match for 22 10 00. | Engineer | Confirmed section numbers. | Unresolved | — | #82
75 | Civil & Site | CS-26 | Landscaping text names features not on this project | Conflict | Low | Restoration area definition. | Engineer | Confirmed restoration areas. | Unresolved | — | #82
76 | Civil & Site | CS-30 | Fire hydrant detail not in the library | Missing information | Low | Only matters if a new fire hydrant is in scope. | Engineer / Setup | Stage Detail W-1 or confirm no new hydrant. | Unresolved | — | #82
77 | Process & Mechanical | Issue 1 | Anoxic basin labeled "Train #4 (Proposed)" | Conflict |  |  | Engineer | Engineer to confirm label | Unresolved | — | #83
78 | Process & Mechanical | Issue 2 | Train 3 zone volumes | Conflict |  |  | Engineer | Confirm; this is the process-guarantee basis (¶1.05 C) | Unresolved | #181, #248 | #83
79 | Process & Mechanical | Issue 3 | Recycle airlift count, location and direction | Conflict |  |  | Engineer | Confirm count, compartment and direction | Unresolved | — | #83
80 | Process & Mechanical | Issue 4 | Clarifier side water depth | Conflict |  |  | Engineer | Confirm the depth behind the G0.7 overflow rates | Unresolved | — | #83
81 | Process & Mechanical | Issue 5 | Wall height and freeboard (low) | Conflict | Low |  | Engineer | Confirm | Unresolved | — | #83
82 | Process & Mechanical | Issue 6 | Air totals (low) | Conflict | Low |  | Engineer | None unless blower sizing is tight | Unresolved | — | #83
83 | Process & Mechanical | Issue 8 | Experience clause names the wrong aeration type | Conflict |  |  | Engineer | Confirm; this sets who qualifies for Equipment Alternate B | Unresolved | — | #83
84 | Process & Mechanical | Issue 9 | Stainless alternates scope (missing) | Missing information |  |  | Engineer | Needs 00 24 13 ¶18–19 (Contract & General) and the 04 Item 18 resolution | Unresolved | #182 | #83
85 | Process & Mechanical | Issue 10 | Recycle pipe size at IE 10.57 | Conflict |  |  | Engineer | Confirm size | Unresolved | — | #83
86 | Process & Mechanical | Issue 30 | Mixers specified in two sections | Conflict |  |  | Engineer | Confirm supplier for mixers, masts and davits, and whether Items 18/19 and Alternate B apply | Unresolved | #32 | #83
87 | Process & Mechanical | Issue 7 | Splitter "3-way" vs four chambers (low) | Conflict | Low |  | Engineer | Confirm | Unresolved (label) | — | #83
88 | Process & Mechanical | Issue 40 | Splitter has no spec section (missing) | Missing information |  |  | Engineer | Name the governing section or confirm the note governs; add submittal and test requirements | Unresolved | #75, #103 | #83
89 | Process & Mechanical | Issue 11 | Pipe brace refers to a sheet not in the set (missing) | Missing information |  |  | Engineer | Confirm 7/C7.2 governs or issue M4.1 | Unresolved | — | #83
90 | Process & Mechanical | Issue 12 | 2W air gap reference and float-controlled valve (missing) | Missing information |  |  | Engineer | Fix the sheet reference; identify the fill valve (Civil & Site C1.3; Electrical & Controls) | Unresolved | #183 | #83
91 | Process & Mechanical | Issue 26 | 2W relief valves | Conflict |  |  | Engineer | Confirm number, location and set points | Unresolved | — | #83
92 | Process & Mechanical | Issue 39 | 2W wet well inlet size | Conflict |  |  | Engineer | Confirm fill line size | Unresolved | — | #83
93 | Process & Mechanical | Issue 13 | UV modules and lamps | Conflict |  |  | Engineer | Confirm G0.7 is superseded | Unresolved | — | #83
94 | Process & Mechanical | Issue 15 | Final effluent size | Conflict |  |  | Engineer | Confirm size and material | Unresolved | #92 | #83
95 | Process & Mechanical | Issue 17 | Digester sludge line sizes | Conflict |  |  | Engineer | Confirm both sizes | Unresolved | #90 | #83
96 | Process & Mechanical | Issue 18 | Sludge flow meter location | Conflict |  |  | Engineer | Confirm meters, service and sizes (Electrical & Controls) | Unresolved | #43, #184 | #83
97 | Process & Mechanical | Issue 32 | UV dose units (low) | Conflict | Low |  | Engineer | Confirm | Unresolved (label) | — | #83
98 | Process & Mechanical | Issue 33 | UV monitor panel distance (low) | Conflict | Low |  | Engineer | Confirm location | Unresolved | #55 | #83
99 | Process & Mechanical | Issue 14 | C6.1 cites a spec section that does not exist | Conflict |  |  | Engineer | Confirm 41 12 13 | Unresolved | — | #83
100 | Process & Mechanical | Issue 16 | Dry vs emulsion polymer | Conflict |  |  | Engineer | Confirm polymer type | Unresolved | — | #83
101 | Process & Mechanical | Issue 22 | Screw conveyor count | Conflict |  |  | Engineer | Confirm number, inlets, length and angle | Unresolved | — | #83
102 | Process & Mechanical | Issue 31 | Ball valve material | Conflict |  |  | Engineer | Confirm material | Unresolved (precedence rule is in the General Conditions) | #188 | #83
103 | Process & Mechanical | Issue 36 | Who controls the digested sludge pump | Conflict |  |  | Engineer | Electrical & Controls to define the interface (26 80 00 ¶3.09 H) | Add. 4 governs VFD location; controlling PLC Unresolved | #61, #189 | #83
104 | Process & Mechanical | Issue 37 | No press field start-up or training (missing) | Missing information |  |  | Engineer | Confirm 01 91 00 covers it or add requirements | Unresolved | #190, #246 | #83
105 | Process & Mechanical | Issue 38 | Potable water for flocculator breather (missing) | Missing information |  |  | Engineer | Confirm water source and backflow protection | Unresolved | #191 | #83
106 | Process & Mechanical | Issue 41 | Carbon feed location, product and storage (missing) | Missing information |  |  | Engineer | Locate the system; specify storage and piping | Unresolved | — | #83
107 | Process & Mechanical | Issue 21 | Sludge pump capacity (low) | Conflict | Low |  | Engineer | None unless the selection is at its limit | Unresolved | — | #83
108 | Process & Mechanical | Issue 24 | Blower design pressure (low) | Conflict | Low |  | Engineer | Confirm system pressure | Unresolved | — | #83
109 | Process & Mechanical | Issue 25 | Wall fan control (low) | Conflict | Low |  | Engineer | Confirm; cross-check E9.3 | Unresolved | #26, #186, #196 | #83
110 | Process & Mechanical | Issue 20 | Launder cover section carries sludge pump text | Conflict |  |  | Engineer | Confirm 10 73 05 ¶3.01 A is void | Add. 4 governs the VFD text (Add. 4 p.1 General, Inferred); deletion Unresolved | — | #83
111 | Process & Mechanical | Issue 23 | Wrong submittal section (low) | Conflict | Low |  | Engineer | Confirm | Unresolved | — | #83
112 | Process & Mechanical | Issue 27 | Wrong painting section (low) | Conflict | Low |  | Engineer | Confirm | Unresolved | #187, #244 | #83
113 | Process & Mechanical | Issue 28 | Globe valve material (low) | Conflict | Low |  | Engineer | Confirm | Unresolved | — | #83
114 | Process & Mechanical | Issue 29 | Polymer flow units and section reference (low) | Conflict | Low |  | Engineer | Confirm flow range and section | Unresolved | — | #83
115 | Process & Mechanical | Issue 34 | Analyzer called "pumps" (low) | Conflict | Low |  | Engineer | Confirm | Unresolved | — | #83
116 | Process & Mechanical | Issue 35 | "22 13 16" cited twice (low) | Conflict | Low |  | Engineer | Confirm | Unresolved | — | #83
117 | Structural & Building | §1 #1 | S2.2 mat slab reinforcing: two "typical for mat slabs this plan" callouts | Conflict |  |  |  | Engineer to state which spacing applies to the UV basin and digester mats | Unresolved — same sheet, no addendum | — | #85
118 | Structural & Building | §1 #2 | Train 3 lap length for Grade 75 bars | Conflict |  |  |  | Engineer to give Grade 75 lap lengths or confirm Grade 60 values govern | Unresolved — both base; Add. 4 reissue of S4.1 leaves Detail 3 unchanged | — | #85
119 | Structural & Building | §1 #3 | Add. 4 reissue revision entries (index vs source) | Conflict |  |  |  | Setup thread to amend 01 log #12 (S-sheet supersession is readable from the revision block) | Source governs; index statement is partly wrong for S sheets | #217 | #51, #85
120 | Structural & Building | §1 #4 | Moist-cure duration | Conflict |  |  |  | Engineer to confirm cure duration for tanks, walls, lids and pads (schedule driver) | Unresolved — same section | — | #85
121 | Structural & Building | §1 #5 | Influent Pump Station hatch | Conflict |  |  |  | Engineer to confirm hatch size and load rating | Unresolved — same section; station drawing C4.1 is Process & Mechanical lane | #218 | #85
122 | Structural & Building | §1 #6 | Handrail and guardrail material | Conflict |  |  |  | Engineer confirmation | Unresolved; likely 05 52 00 as the dedicated section (Inferred) | #34, #219 | #85
123 | Structural & Building | §1 #7 | Grating type and support angles at UV basin and digester | Conflict |  |  |  | Engineer to confirm grating type over the digester and the support-angle material | Unresolved | #57, #220 | #85
124 | Structural & Building | §1 #8 | Blower Building interior insulation and finish assembly | Conflict |  |  |  | Architect or engineer to state where each assembly applies (walls vs roof) | Unresolved | — | #85
125 | Structural & Building | §1 #9 | Lockset type and keying standard | Conflict |  |  |  | Owner to confirm keying standard; engineer to confirm lockset type | Unresolved; Part 4 schedule likely governs as more specific (Inferred) | — | #85
126 | Structural & Building | §2 #1 | Door 101B height | Missing information |  |  |  | Native A1.1 or engineer confirmation | Unresolved | — | #85
127 | Structural & Building | §2 #2 | Bid Item 9 — Structural Concrete (Extra Work, approx. 10 CY) | Missing information |  |  |  | Contract & General lane or Merge to state what Item 9 pays for | Unresolved | #133, #221 | #85
128 | Structural & Building | §2 #3 | Which structures are "hydraulic structures" | Missing information |  |  |  | Engineer confirmation of the hydraulic-structure list | Inferred | — | #85
129 | Structural & Building | §2 #4 | Identity of the "Drain Pump Station" | Missing information |  |  |  | Civil & Site or Process & Mechanical lane / Merge to identify the station and its civil sheet | Unresolved | #37, #222 | #85
130 | Structural & Building | §2 #5 | Generator on S2.4 — permanent or temporary | Missing information |  |  |  | Electrical & Controls lane / Merge to tie the slab to the permanent standby generator or the temporary back-up generator | Unresolved | #65, #223 | #85
131 | Structural & Building | §2 #6 | S2.3 perimeter grade beam bar size | Missing information |  |  |  | Native S2.3 (Add. 4 reissue) | Unresolved | — | #85
132 | Structural & Building | §2 #7 | Structures named in 03 30 00 but not in the sheet titles | Missing information |  |  |  | Engineer to confirm the structures the formwork submittal and broom finish apply to | Unresolved | #258 | #85
133 | Structural & Building | §2 #8 | Section 04 60 00 (grouting) does not exist | Missing information |  |  |  | Engineer to name the governing grout requirement (03 40 00 ¶2.02 F and 05 50 00 ¶2.01 E.7–8 are candidates — Inferred) | Unresolved | — | #85
134 | Structural & Building | §2 #9 | No spec coverage for footing-perimeter XPS and EIFS | Missing information |  |  |  | Engineer or architect to add or point to a section for R-10 XPS and Dryvit EIFS | Unresolved | — | #85
135 | Structural & Building | §2 #10 | WSDOT references (external, not staged) | Missing information |  |  |  | Stage the cited WSDOT sections or accept by reference | Unresolved: external reference, not staged | — | #85
136 | Structural & Building | §2 #11 | Door hardware group assignment | Missing information |  |  |  | Confirm group per door on the hardware schedule submittal | Inferred | — | #85
137 | Structural & Building | §2 #12 | Sheet C8.1 (exterior door stop detail) | Missing information |  |  |  | Engineer to issue or delete the reference | Unresolved | — | #52, #85
138 | Structural & Building | §2 #13 | Blower Building painting reference | Missing information |  |  |  | Engineer to state the paint system for the other Blower Building surfaces, e.g., the painted exposed-structure ceiling on A1.1 | Unresolved | — | #85
139 | Structural & Building | §2 #14 | Blower Building floor sealer | Missing information |  |  |  | Engineer to name the floor sealer product and confirm it with the damp-cure requirement | Unresolved | — | #85

## Settled
Lane | Lane ID | Item | Basis
Contract & General | 1.7 | Stale page numbers in 00 43 93 for the 00 53 00 attachments; content located | Record only — Verified
Contract & General | 1.13 | 00 73 00 pp.98–121 repeat the 00 53 00 Ecology insert word for word (99.8% word match) | Record only — Verified
Contract & General | 1.18 | 01 66 00 body is the 01 60 00 text word for word | Record only — Verified
Contract & General | 1.22 | Clean water leakage test list is repeated with different names | Record only — Verified
Contract & General | 1.25 | QA plan labels the construction phase "October 2022 – April 2024"; its own list runs to Oct 16, 2024 | Record only — Verified (SC 15 governs — Inferred)
Electrical & Controls | Issues #16 | Existing 208V utility transformer: the Utility removes it (26 05 00 ¶3.03 F.1.a, main spec p.279) — Issues #16. | Settled (lane)
Electrical & Controls | — | Train 1 flow meter: "future project – not in this project"; Phase I provides transmitter space only (E10.2 item 2, plans_12 p.7). | Settled (lane)
Electrical & Controls | Issues #8 | MCC length: Add. 4 p.1 Clarification 4 (eight 20-in sections, 160 in) governs over the seven sections, 140 in, on E9.1; the added section contents are left to the contractor layout (E9.1 general note 1) — Issues #8. | Settled (lane)
Electrical & Controls | — | Flow meter model: Add. 4 p.2 (26 80 00 ¶2.04 D) Promag W400 governs over L400; E4.1, E4.3, E5.1 and E10.2 already show W400. | Settled (lane)
Electrical & Controls | — | Sludge and 2W pump VFDs: Add. 4 p.2 (22 13 36 and 43 22 10 ¶2.01 A) puts them in the MCC under PLC control; E6.1 and E9.1 already match. | Settled (lane)
Electrical & Controls | — | VFD speed control: over Ethernet, no analog speed wiring (E9.2 key note 2, plans_12 p.4); E7.7 has no analog speed outputs. | Settled (lane)
Electrical & Controls | Issues #15 | 26 80 00 repeats ¶2.01 and ¶2.02 after ¶2.05; cite those paragraphs by page (pp.357, 367, 370) — Issues #15. | Settled (lane)
Electrical & Controls | — | Running headers: 26 36 00 reads "26 30 00" (02 log item 4) and 26 80 00 reads "INSTRUMENTATION AND CONTROL" (02 log item 6); body section numbers govern. | Settled (lane)
Electrical & Controls | — | Sheet titles that differ from the cover index (E0.4, E1.1, E3.1, E5.1, E8.2) are carried in the 01 log; the A1.1/A1.2 relocation of the MCC and main PLC panel belongs to the Structural & Building stack (cited flags). | Settled (lane)
Civil & Site | CS-06 | Pipe ID 10: base 2-in Sch. 80 PVC (plans_3Part-1 p.1) changed to 3-in HDPE by Add. 4 (Add. 4 p.7). Add. 4 governs; Ledger uses the Add. 4 value. (Verified-Visual) | Closed (lane)
Civil & Site | CS-12 | C2.5 fence height mark reads 6" (plans_3Part-8 p.1); 02 83 00 ¶1.01 A says all chain-link fence is 6 ft plus barbed wire, 7 ft total (main spec p.163). Carried as 6 ft — Inferred; confirm on the native PDF. (Inferred) | Closed (lane)
Process & Mechanical | Issue 19 | Building separation | Settled: Add. 4 governs (C6.3 not reissued)